SECTION 223400 –  CONDENSING GAS - FIRED DOMESTIC WATER HEATERS

PART 1 - GENERAL

1.1	 RELATED DOCUMENTS

- Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2	SUMMARY

- This Section includes domestic water heating packaged system construction, components, required trim, controls, and accessories necessary for domestic water heating.

1.3	REFERENCES

- Comply with applicable Codes/Standards of:

  - American Society of Mechanical Engineers (ASME).

  - National Board of Water heater and Pressure Vessel Inspectors (NBBPVI).

  - National Electrical Manufacturers' Association (NEMA).

#### Underwriters Laboratories (UL)

#### Local air quality management district emission requirements.

1.4	SUBMITTALS

- Comply with provisions of Section 01300 - SUBMITTALS.

- Manufacturer's descriptive literature, operating instructions, maintenance and repair data.

- Three Dimensional Fabrication Drawings showing dimensions and electrical requirements.

- Submit water heater factory testing certificate.

1.5	QUALITY ASSURANCE

- Provide factory tests to check construction integrity and control function of the complete system.

- Water Heater shall be certified to operate at minimum efficiency of 85 percent at 100 percent of firing rate.

- Installed materials not meeting specification requirements of the Contract Documents will be subject to removal and replacement

1.6	COORDINATION

- Coordinate size and location of concrete bases with Architectural and Structural Drawings.

1.7	WARRANTY

- Provide warranty on internal piping, valves, electrical wiring, other inter-connecting components and structural frames against defects in the original materials and workmanship for a period of 12 months from the date of equipment start-up or 18 months from date of shipment, whichever is less.

PART 2 - PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS

- Contractor to furnish and install a pre-assembled, pre-piped, Domestic Water Heating package as manufactured by “FlowTherm Systems,” or approved equal. Alternate package system manufacturers must be able to demonstrate a successful history of manufacturing similar systems for a minimum of 10 years.

2.2	DOMESTIC WATER HEATING SKID PACKAGE

A.	General:

- The packaged system shall include, as a minimum, the following components:

  - Two (2) Condensing Domestic hot water heaters.

  - Two (2) Water heater circulating pumps.

  - One (1) Expansion tank.

  - One (1) Hot water storage tank

  - Power/Control panel.

  - Building domestic hot water recirculation pump

  - Thermometers, gauges, isolation valves and inter-connecting piping.

  - All components shall be mounted on a structural steel baseplate covered with ¼” steel decking.  The entire assembled unit shall be primed with red oxide and finished with a heavy coat of exterior-grade industrial enamel.  It is acceptable to provide the packaged system as multiple skids which are field installed directly adjacent to one another with factory-supplied interconnecting piping and electrical.

  - The package shall be designed to supply, and control the domestic hot water within the flow and temperature conditions specified for the system.

  - The Package shall be UL Listed according to UL Standard #778 for Pumping Systems.

  - Performance:  Refer to Schedule on Drawings.

B.         DOMESTIC WATER HEATERS (WH-1 & WH-2)

The water heater shall be a Laars NeoTherm Model NTV______, rated at __________ BTU/hr input and __________ BTU/hr output. The water heater shall modulate 20-100% of full fire. The unit(s) shall be design-certified to comply with the current edition of the Harmonized ANSI Z21.13 / CSA 4.3 Standard for Gas Water Heaters.  The unit(s) shall be designed and constructed in accordance with the ASME Water heater & Pressure Vessel Code, Section IV requirements for 160 psi (1103 kPa) maximum working pressure, and shall bear the ASME "H" Stamp and be listed by the National Board. d.

The water heater shall be listed with AHRI (Air Conditioning, Heating and Refrigeration Institute). The water heater shall have a minimum thermal efficiency of 95%. The unit(s) shall be constructed to comply with the efficiency requirements of the latest edition of ASHRAE Standard 90.1.

The water heater shall be certified for placement indoors and outdoors, where freezing conditions do not exist. The heater must meet ANSI Z21.10.3-2013, section 5.24 wind test and section 5.30 rain test for outdoor installations.

The water heater shall be equipped with an ASME certified pressure relief valve set at 75psi 517 (kPa). Optional pressure relief valves with settings of 30psi (207kPa), 50psi (345 kPa), 60psi (413 kPa), 125psi (861 kPa) or 150psi (1034 kPa) shall be available.

The water tube heat exchanger shall be stainless steel, rated for 160 psi (1103 kPa) working pressure. The heat exchanger shall be a low water volume design, welded construction, with no gaskets, o-rings, or bolts in the header. Heat exchanger shall be accessible for visual inspection and cleaning of all internal surfaces. The water heater shall be fully condensing design with built-in condensate drain and trap. The heat exchanger shall have a limited five-year warranty.

Each water heater shall be fully test fired, (with water, gas, and venting connected), and all safety components tested, at the factory.

The water heater shall be sealed combustion, and removal of jacket panels shall not affect the combustion seal. The heater jacket shall be a unitized shell finished with acrylic thermo-set paint baked at not less than 325°F (163°C). The frame shall be constructed of galvanized steel for strength and protection. Chamber shall include a sight glass for viewing flame. Heater shall be certified for zero clearance to combustible surfaces

Water heater shall operate on 4-13" W.C. gas pressure, and shall need no component changes to operate at high altitude, up to 10,000 feet.

The water heater shall use a premix burner with a stainless steel woven metal fiber wrap, and a negative pressure gas valve to burn cleanly, with NOx emissions not exceeding 10ppm. The water heater shall meet the emissions requirements of SCAQMD 2012.

The water heater shall be designed for vertical or horizontal Category IV venting, up to 100 equivalent feet in the specified diameter with PVC, CPVC or stainless steel vent material.  Air may be taken from the room, or ducted directly to the water heater, using up to 100 equivalent feet of 4" ABS, PVC, CPVC or galvanized pipe. The water heater shall be shipped with PVC sidewall vent and air terminals, for use with horizontal systems.  The first section of CPVC vent pipe shall be shipped with each water heater.

The water heater control shall be an integrated electronic PID temperature and ignition control with large touchscreen and color display and shall control the water heater operation and firing rate. The water heater display shall be visible without the removal of any jacket panels or control panels. The control shall have the ability to control the water heater pump, system pump and indirect domestic water pump, each with delay and exercise features.

The control shall have built-in outdoor reset feature with customizable reset curves, based on the outdoor temperature and desired system water temperature. The water heater shall be shipped with the outdoor reset sensor, as standard equipment.

The control shall have dry alarm contacts for ignition failure. The control shall monitor flue gas temperature and shall stop the water heater from firing if temperature is excessive.

Allowable control adjustments shall include: enable/disable; water heater temperature setpoint; manual firing rate control; pump delay time; pump exercise interval; outdoor reset selection; warm weather shutdown; and anti-short cycle feature.

The water heater controller shall be able to cascade and lead-lag the water heaters without an additional system controller. The burners shall be controlled to keep each one in the lowest firing rate possible, based on system demand, to maximize efficiency.

In addition to adjustable parameters, the master display shall also be able to show information about the following for each water heater it is monitoring:

• burner control

• demand and modulation

• inlet temperature

• fan speed

• domestic hot water temp

• water heater pump

• flame detection

• statistics

• stack limit

• frost protection

The control shall have the ability to accept a 4-20mA or 0-10VDC input connection from an external control or building automation system, to modulate the flame.

The controller shall be able to send information through a BACnet connection, including (but not limited to) inlet and outlet water temperatures, stack temperature, status of sensors, fan speed, set points, remote control input, burner status, lockout codes, alarm reasons, system pump status, water heater pump status and domestic water pump status.

Control diagnostics shall include, at a minimum, the following: ignition failure, grounded flame rod, safety chain interrupt, water heater high limit exceeded, domestic water high limit exceeded, temperature rise limit exceeded, stack limit exceeded, pressure sensor fault, combustion pressure fault, blocked air intake, sensor errors (open or shorted), 24VAC voltage low or high, modulation fault, pump fault, AC input phases reversed, and fan speed proving rate failure.

C.    EXPANSION TANK

The water heater heating package shall include (1) ASME pressurized expansion tank, Bell & Gossett PTA-Series diaphragm style construction. The tank shall be factory pre-charged to 40 psig.  The diaphragm shall be constructed of FDA approved butyl and polypropylene liner.  The tank shall have a stainless steel NPT system connection with a charging valve connection to facilitate on-site charging of the tank to meet system requirements. The tank must be constructed in accordance with Section VIII of the ASME Water heater and Pressure Vessel Code.

D.   HOT WATER STORAGE TANK

The hot water storage tank shall be constructed of carbon steel and glass lined with a minimum of 10 mils of untonium glass suitable for temperatures up to 180°F.  Lining shall extend to the nozzle openings.  The tank shall be built and stamped to ASME Code Section VIII requirements for 125 PSIG minimum working pressure.  A manhole with 12” X 16” opening shall be provided.  All tank connections 3” and larger shall be flanged.  All connections 2 1/2” and smaller shall be threaded stainless steel.  The tank shall be furnished as either vertical or horizontal as indicated on the drawings.  Provide welded saddles for horizontal tanks and heavy angle iron legs with mounting pads for vertical tanks.  The tank shall be pre-insulated with sprayed-on polyurethane foam with topcoat.

The insulation shall be polyurethane foam and have a minimum rating of R-16.

E.    POWER PANEL

The Power panel shall be NEMA 1 for indoor service OR NEMA 3R with deadfront door for outdoor service and have a non-fused main power disconnect to provide power to the water heaters and the water heater circulating pumps as well as the building domestic hot water recirculating pump. Individual local power disconnects shall be provided for all powered equipment. The water heater circulating pumps are controlled by the water heater controller via magnetic starters. The building domestic hot water recirculating pump is controlled by a local aquastat to maintain recirculating loop temperature (adjustable).

F.    BUILDING DOMESTIC HOT WATER RECIRCULATION PUMP

A building domestic hot water recirculation pump shall be piped to the storage tank and shall be controlled by an adjustable aquastat to maintain a minimum domestic hot water supply loop temperature (adjustable). The pump shall be low lead bronze or stainless steel as required by local plumbing code.

G.    ISOLATION VALVES

Isolation valves shall be provided to service of all major components of the water heater heating package. These valves will facilitate the removal of a component for servicing without the need of draining the heating water from the system piping.

H.     Natural gas supply piping to each appliance by installing contractor

I.     Vents off regulators and relief valves shall be individual and be provided by installing 		         	        contractor.

J.     Hydrostatic Test:  Shop-assembled pressure parts of the water heater shall be hydrostatically tested at the factory at a pressure of 1.25 times the design pressure.  A manufacturer's Data Report to confirm compliance with ASME Code requirements shall be furnished by the water heater manufacturer.

K.     Functionality Test:  Perform a factory functional test of all system electrical components and skid wiring prior to shipment.

PART 3 - EXECUTION

3.1	WATER HEATER INSTALLATION

- Place and mount skid on a level concrete equipment pad

- Make utility and system connections as described in this section.

- Water heater Venting – each water heater shall be vented according to manufacturer’s recommendation and shall conform to the requirements of the National Fuel Gas Code (American Standard Z223.1-Latest Edition).

- Gas Regulator and Gas Train Vents – Pipe through roof or wall to atmosphere

E.	Provide services of manufacturer's representative to supervise rigging, hoisting, and 			installation of the water heater.

F.		Coordinate electrical and control work.

G.	Install ship loose items, such as sensors, sight glasses, safety valves, and gauges.

H.	Pipe safety valves to floor drain.

3.3	START UP

- Provide services of manufacturer's representative to inspect water heater after installation is complete and submit report prior to start up, verifying installation is in accordance with specifications and manufacturer's recommendations.

  - The package manufacturer shall provide the services of a trained technician to assist in starting up, adjustment and operation of water heater and firing equipment and all other equipment furnished by the water heater manufacturer.  In addition, the technician shall perform requisite field tests and instruct the Owner's operating personnel in the proper operation and maintenance of the unit.

END OF SECTION