SECTION 223400 –  NON-CONDENSING GAS-FIRED DOMESTIC WATER HEATERS

PART 1 - GENERAL

1.1	 RELATED DOCUMENTS

- Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2	SUMMARY

- This Section includes domestic water heating packaged system construction, components, required trim, controls, and accessories necessary for domestic water heating.

1.3	REFERENCES

- Comply with applicable Codes/Standards of:

  - American Society of Mechanical Engineers (ASME).

  - National Board of Water heater and Pressure Vessel Inspectors (NBBPVI).

  - National Electrical Manufacturers' Association (NEMA).

#### Underwriters Laboratories (UL)

#### Local air quality management district emission requirements.

1.4	SUBMITTALS

- Comply with provisions of Section 01300 - SUBMITTALS.

- Manufacturer's descriptive literature, operating instructions, maintenance and repair data.

- Three Dimensional Fabrication Drawings showing dimensions and electrical requirements.

- Submit water heater factory testing certificate.

1.5	QUALITY ASSURANCE

- Provide factory tests to check construction integrity and control function of the complete system.

- Water Heater shall be certified to operate at minimum efficiency of 85 percent at 100 percent of firing rate.

- Installed materials not meeting specification requirements of the Contract Documents will be subject to removal and replacement

1.6	COORDINATION

- Coordinate size and location of concrete bases with Architectural and Structural Drawings.

1.7	WARRANTY

- Provide warranty on internal piping, valves, electrical wiring, other inter-connecting components and structural frames against defects in the original materials and workmanship for a period of 12 months from the date of equipment start-up or 18 months from date of shipment, whichever is less.

PART 2 - PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS

- Contractor to furnish and install a pre-assembled, pre-piped, Domestic Water Heating package as manufactured by “FlowTherm Systems,” or approved equal. Alternate package system manufacturers must be able to demonstrate a successful history of manufacturing similar systems for a minimum of 10 years.

2.2	DOMESTIC WATER HEATING SKID PACKAGE

A.    General:

- The packaged system shall include, as a minimum, the following components:

  - Two (2) Natural gas fired domestic hot water heaters.

  - Two (2) Water heater circulating pumps.

  - One (1) Expansion tank.

  - One (1) Hot water storage tank

  - Power/Control panel.

  - Building domestic hot water recirculation pump

  - Thermometers, gauges, isolation valves and inter-connecting piping.

  - All components shall be mounted on a structural steel baseplate covered with ¼” steel decking.  The entire assembled unit shall be primed with red oxide and finished with a heavy coat of exterior-grade industrial enamel.  It is acceptable to provide the packaged system as multiple skids which are field installed directly adjacent to one another with factory-supplied interconnecting piping and electrical.

  - The package shall be designed to supply, and control the domestic hot water within the flow and temperature conditions specified for the system.

  - The Package shall be UL Listed according to UL Standard #778 for Pumping Systems.

  - Performance:  Refer to Schedule on Drawings.

B.    DOMESTIC WATER HEATERS (WH-1 & WH-2)

The water heater shall be a Laars Model No. MT2V_________ pump-mounted water heaters rated at the input and output shown on the schedule.  The unit(s) shall be design certified to comply with the current edition of the Harmonized ANSI Z21.10.3 / CSA 4.3 Standard for Gas Water Heaters, and shall be design certified for both indoor and outdoor use.  The unit(s) shall be designed and constructed in accordance with the ASME Boiler & Pressure Vessel Code, Section IV requirements for 160 psi (1103 kPa) working pressure, and shall bear the ASME “H” Stamp.  The unit(s) shall be constructed to comply with the efficiency requirements of the latest edition of ASHRAE Standard 90.1.

The water tube heat exchanger shall be a straight tube design with ten 7/8" (22mm) inner diameter integral finned copper tubes.  The tubes shall be rolled directly into glass-lined cast iron headers, rated for 160 psi (1103 kPa) working pressure. The heat exchanger shall be a low water volume design.  All gaskets shall be non-metallic, outside the jacket, and separated from the combustion chamber by at least 3.5" (89mm) to eliminate deterioration from heat.  Headers shall have covers permitting visual inspection and cleaning of all internal surfaces.  The heat exchanger shall have a ten-year warranty.

The piping side header shall have removable flanges, and the water heater design shall permit removal of the complete heat exchanger for service from either the front or top, to facilitate maintenance.

The heater shall come complete with a volute-mounted pump sized to provide the correct heater flow rate, for the heater and 30 feet (9.1m) of full-sized piping.  Each unit shall have a pump time delay.  The pump time delay shall be adjustable from 0.1 to 10 minutes for continued pump circulation after the call for heat has been satisfied, to remove residual heat from the unit’s combustion chamber.

The units shall use a proven hot surface ignition with a 15 second pre-purge cycle to clean out the combustion chamber.  Upon a call for heat, if a fame is not detected, the ignition module shall attempt two more times before locking out, and requiring manual reset. If there is a loss of fame signal during a call for heat, the ignition control shall attempt three re-ignition cycles before locking out.

The control circuit shall be 24V.  Unit shall be 120V, single phase, less than 12 Amps. Mounted pump shall be 120V, single-phase. Burners shall be multi-port design, and shall be constructed of high temperature stainless steel.  The burners shall be designed to mix air and gas, and burn cleanly with NOx emissions not exceeding 10ppm.  Burners shall be in easily-removable burner tray assemblies with no more than 4 burners per tray.

The combustion chamber shall be lined with lightweight, ceramic fiberboard insulation to retain heat, and shall be approved for service temperatures of not less than 2000°F (1093°C).  The outer jacket shall be a unitized shell finished with acrylic thermo-set paint baked at not less than 325°F (163°C).

The frame shall be constructed of galvanized steel for strength and protection.  Chamber shall include a sight glass for viewing fame. Heaters shall have a forced draft design and shall meet a minimum 85% thermal efficiency.  The unit shall be designed for vertical venting with standard B-vent as a fan-assisted Category I appliance, and for horizontal venting as a Category III appliance and shall not require an external draft hood.  The unit shall accept ducted combustion air, or shall be able to pull combustion air from the room.

The heater shall have two firing stages, and the heater shall have connections for an external staging control, and a selector switch to enable the user to choose between the water heater’s staging control or a field-supplied staging control, without bypassing any of the heater’s safety controls.

Unit(s) shall have multiple gas trains, such that each gas train shall have a maximum input of 399,000 BTU/hr.  Each gas train shall have a gas shutoff valve and main gas valve with built-in redundant valve seats and gas regulator.  Flanges or unions shall be used before and after each main gas valve, to permit easy removal of each gas valve, gas train and burner tray assembly from the front of the unit.

The heater shall be provided with an integral, washable combustion air filter.  The air filter shall provide 83% arrestence to protect the burners and blower(s) from debris.  The air filter shall be constructed of open-cell polyurethane foam.

Heater shall include as standard equipment the following controls and trim:

• ASME 160 psi working pressure heat exchanger

• ASME “H” stamp

• Glass-lined cast iron headers

• 125 psi (861 kPa) ASME rated pressure relief valve

• Flow switch

• Intake air filter

• Removable burner trays

• Stainless steel burners

• Built-in draft fan(s) for Category I or III venting

• Burner site glass

• 24V control system

C.    EXPANSION TANK

The water heater heating package shall include (1) ASME pressurized expansion tank, Bell & Gossett PTA-Series diaphragm style construction. The tank shall be factory pre-charged to 40 psig.  The diaphragm shall be constructed of FDA approved butyl and polypropylene liner.  The tank shall have a stainless steel NPT system connection with a charging valve connection to facilitate on-site charging of the tank to meet system requirements. The tank must be constructed in accordance with Section VIII of the ASME Water heater and Pressure Vessel Code.

D.   HOT WATER STORAGE TANK

The hot water storage tank shall be constructed of carbon steel and glass lined with a minimum of 10 mils of untonium glass suitable for temperatures up to 180°F.  Lining shall extend to the nozzle openings.  The tank shall be built and stamped to ASME Code Section VIII requirements for 125 PSIG minimum working pressure.  A manhole with 12” X 16” opening shall be provided.  All tank connections 3” and larger shall be flanged.  All connections 2 1/2” and smaller shall be threaded stainless steel.  The tank shall be furnished as either vertical or horizontal as indicated on the drawings.  Provide welded saddles for horizontal tanks and heavy angle iron legs with mounting pads for vertical tanks.  The tank shall be pre-insulated with sprayed-on polyurethane foam with topcoat.

The insulation shall be polyurethane foam and have a minimum rating of R-16.

E.    POWER PANEL

The Power panel shall be NEMA 1 for indoor service OR NEMA 3R with deadfront door for outdoor service and have a non-fused main power disconnect to provide power to the water heaters and the water heater circulating pumps as well as the building domestic hot water recirculating pump. Individual local power disconnects shall be provided for all powered equipment. The water heater circulating pumps are controlled by the water heater controller via magnetic starters. The building domestic hot water recirculating pump is controlled by a local aquastat to maintain recirculating loop temperature (adjustable).

F.    BUILDING DOMESTIC HOT WATER RECIRCULATION PUMP

A building domestic hot water recirculation pump shall be piped to the storage tank and shall be controlled by an adjustable aquastat to maintain a minimum domestic hot water supply loop temperature (adjustable). The pump shall be low lead bronze or stainless steel as required by local plumbing code.

G.    ISOLATION VALVES

Isolation valves shall be provided to service of all major components of the water heater heating package. These valves will facilitate the removal of a component for servicing without the need of draining the heating water from the system piping.

H. 	Natural gas supply piping to each appliance by installing contractor

I.	Vents off regulators and relief valves shall be individual and be provided by installing 		         	contractor.

J.	Hydrostatic Test:  Shop-assembled pressure parts of the water heater shall be hydrostatically tested at the factory at a pressure of 1.25 times the design pressure.  A manufacturer's Data Report to confirm compliance with ASME Code requirements shall be furnished by the water heater manufacturer.

K.     	Functionality Test:  Perform a factory functional test of all system electrical components 	and skid wiring prior to shipment.

PART 3 - EXECUTION

3.1	WATER HEATER INSTALLATION

- Place and mount skid on a level concrete equipment pad

- Make utility and system connections as described in this section.

- Water heater Venting – each water heater shall be vented according to manufacturer’s recommendation and shall conform to the requirements of the National Fuel Gas Code (American Standard Z223.1-Latest Edition).

- Gas Regulator and Gas Train Vents – Pipe through roof or wall to atmosphere

- Provide services of manufacturer's representative to supervise rigging, hoisting, and installation of the water heater.

- Coordinate electrical and control work.

- Install ship loose items, such as sensors, sight glasses, safety valves, and gauges.

- Pipe safety valves to floor drain.

3.3	START UP

- Provide services of manufacturer's representative to inspect water heater after installation is complete and submit report prior to start up, verifying installation is in accordance with specifications and manufacturer's recommendations.

  - The package manufacturer shall provide the services of a trained technician to assist in starting up, adjustment and operation of water heater and firing equipment and all other equipment furnished by the water heater manufacturer.  In addition, the technician shall perform requisite field tests and instruct the Owner's operating personnel in the proper operation and maintenance of the unit.

END OF SECTION